## Sheet1
address | comment | datatype | functioncode | rir | rhr | psr | pmr | format | len | id | key | write | AGW23
设备类型 |  |  |  | 0 | 0 | 0 | 0
0x0000 | 网关设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 | 21：WiFi版本网关 22：以太网RJ45网关 23: 4G网关 24: 4G网关路由 | 1 | GDT | gateway_device_type | 0 | 1
0x0001 | 网关从设备个数（配置的总个数） | ushort | 0x04 | 0 | 1 | 0 | 0 | 范围0-32个 | 1 | SCC | switch_count_configured | 0 | 1
0x0002 | 网关在线从设备个数（第一次上电轮询的总设备在线个数，后续掉线的从机设备通过通信故障位示，重新轮询在线从设备个数的方式：1，断电上电，2，网关按键，3，上位机发指令） | ushort | 0x04 | 0 | 1 | 0 | 0 | 范围0-32个 | 1 | SCO | switch_count_online | 0 | 1
| 网关的设备ID号（8个字节） | hex | 0x04 | 0 | 1 | 0 | 0 | 1，最高byte为FF 2，第二个byte为随机数 3，其他为出厂时间 | 4 | GID | gateway_ID | 0 | 1
0x0007 | 第[1]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 | 断路器设备类型： 1:1P， 2:1PN， 3:1PNL, 4:3P， 5:3PN， 6:3PNL， 12:2P， 16:4P | 1 | SDT1 | SDT | 0 | 1
0x0008 | 第[1]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 | 1-247 | 1 | SA1 | SA | 0 | 1
0x0009 | 第[1]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID1 | SID | 0 | 1
0x000D | 第[2]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT2 | SDT | 0 | 1
0x000E | 第[2]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA2 | SA | 0 | 1
0x000F | 第[2]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID2 | SID | 0 | 1
0x0013 | 第[3]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT3 | SDT | 0 | 1
0x0014 | 第[3]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA3 | SA | 0 | 1
0x0015 | 第[3]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID3 | SID | 0 | 1
0x0019 | 第[4]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT4 | SDT | 0 | 1
0x001A | 第[4]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA4 | SA | 0 | 1
0x001B | 第[4]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID4 | SID | 0 | 1
0x001F | 第[5]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT5 | SDT | 0 | 1
0x0020 | 第[5]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA5 | SA | 0 | 1
0x0021 | 第[5]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID5 | SID | 0 | 1
0x0025 | 第[6]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT6 | SDT | 0 | 1
0x0026 | 第[6]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA6 | SA | 0 | 1
0x0027 | 第[6]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID6 | SID | 0 | 1
0x002B | 第[7]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT7 | SDT | 0 | 1
0x002C | 第[7]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA7 | SA | 0 | 1
0x002D | 第[7]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID7 | SID | 0 | 1
0x0031 | 第[8]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT8 | SDT | 0 | 1
0x0032 | 第[8]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA8 | SA | 0 | 1
0x0033 | 第[8]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID8 | SID | 0 | 1
0x0037 | 第[9]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT9 | SDT | 0 | 1
0x0038 | 第[9]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA9 | SA | 0 | 1
0x0039 | 第[9]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID9 | SID | 0 | 1
0x003D | 第[10]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT10 | SDT | 0 | 1
0x003E | 第[10]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA10 | SA | 0 | 1
0x003F | 第[10]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID10 | SID | 0 | 1
0x0043 | 第[11]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT11 | SDT | 0 | 1
0x0044 | 第[11]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA11 | SA | 0 | 1
0x0045 | 第[11]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID11 | SID | 0 | 1
0x0049 | 第[12]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT12 | SDT | 0 | 1
0x004A | 第[12]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA12 | SA | 0 | 1
0x004B | 第[12]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID12 | SID | 0 | 1
0x004F | 第[13]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT13 | SDT | 0 | 1
0x0050 | 第[13]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA13 | SA | 0 | 1
0x0051 | 第[13]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID13 | SID | 0 | 1
0x0055 | 第[14]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT14 | SDT | 0 | 1
0x0056 | 第[14]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA14 | SA | 0 | 1
0x0057 | 第[14]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID14 | SID | 0 | 1
0x005B | 第[15]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT15 | SDT | 0 | 1
0x005C | 第[15]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA15 | SA | 0 | 1
0x005D | 第[15]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID15 | SID | 0 | 1
0x0061 | 第[16]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT16 | SDT | 0 | 1
0x0062 | 第[16]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA16 | SA | 0 | 1
0x0063 | 第[16]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID16 | SID | 0 | 1
0x0067 | 第[17]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT17 | SDT | 0 | 1
0x0068 | 第[17]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA17 | SA | 0 | 1
0x0069 | 第[17]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID17 | SID | 0 | 1
0x006D | 第[18]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT18 | SDT | 0 | 1
0x006E | 第[18]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA18 | SA | 0 | 1
0x006F | 第[18]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID18 | SID | 0 | 1
0x0073 | 第[19]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT19 | SDT | 0 | 1
0x0074 | 第[19]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA19 | SA | 0 | 1
0x0075 | 第[19]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID19 | SID | 0 | 1
0x0079 | 第[20]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT20 | SDT | 0 | 1
0x007A | 第[20]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA20 | SA | 0 | 1
0x007B | 第[20]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID20 | SID | 0 | 1
0x007F | 第[21]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT21 | SDT | 0 | 1
0x0080 | 第[21]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA21 | SA | 0 | 1
0x0081 | 第[21]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID21 | SID | 0 | 1
0x0085 | 第[22]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT22 | SDT | 0 | 1
0x0086 | 第[22]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA22 | SA | 0 | 1
0x0087 | 第[22]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID22 | SID | 0 | 1
0x008B | 第[23]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT23 | SDT | 0 | 1
0x008C | 第[23]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA23 | SA | 0 | 1
0x008D | 第[23]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID23 | SID | 0 | 1
0x0091 | 第[24]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT24 | SDT | 0 | 1
0x0092 | 第[24]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA24 | SA | 0 | 1
0x0093 | 第[24]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID24 | SID | 0 | 1
0x0097 | 第[25]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT25 | SDT | 0 | 1
0x0098 | 第[25]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA25 | SA | 0 | 1
0x0099 | 第[25]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID25 | SID | 0 | 1
0x009D | 第[26]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT26 | SDT | 0 | 1
0x009E | 第[26]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA26 | SA | 0 | 1
0x009F | 第[26]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID26 | SID | 0 | 1
0x00A3 | 第[27]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT27 | SDT | 0 | 1
0x00A4 | 第[27]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA27 | SA | 0 | 1
0x00A5 | 第[27]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID27 | SID | 0 | 1
0x00A9 | 第[28]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT28 | SDT | 0 | 1
0x00AA | 第[28]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA28 | SA | 0 | 1
0x00AB | 第[28]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID28 | SID | 0 | 1
0x00AF | 第[29]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT29 | SDT | 0 | 1
0x00B0 | 第[29]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA29 | SA | 0 | 1
0x00B1 | 第[29]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID29 | SID | 0 | 1
0x00B5 | 第[30]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT30 | SDT | 0 | 1
0x00B6 | 第[30]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA30 | SA | 0 | 1
0x00B7 | 第[30]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID30 | SID | 0 | 1
0x00BB | 第[31]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT31 | SDT | 0 | 1
0x00BC | 第[31]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA31 | SA | 0 | 1
0x00BD | 第[31]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID31 | SID | 0 | 1
0x00C1 | 第[32]个从机设备类型 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SDT32 | SDT | 0 | 1
0x00C2 | 第[32]个从机设备地址 | ushort | 0x04 | 0 | 1 | 0 | 0 |  | 1 | SA32 | SA | 0 | 1
0x00C3 | 第[32]个从机设备设备ID号 | hex | 0x04 | 0 | 1 | 0 | 0 |  | 4 | SID32 | SID | 0 | 1
0x00C7 | 当前网络状态 | ushort | 0x04 | 0 | 1 | 0 | 0 | 0：断网，1：联网中，2：联网成功，3：热点模式，4:4G卡没有插入 | 1 | id103 | key103 | 0 | 1
0x00C8 | 4G模组自检结果（必须插入4G卡，每次断电上电自检） | ushort | 0x04 | 0 | 1 | 0 | 0 | 0：自检失败，1：自检成功 | 1 | id104 | key104 | 0 | 1
0x00C9 | 4G信号强度（运行中获取，其他为注册时候获取，最大值注册时获取，后面就周期获取） | ushort | 0x04 | 0 | 1 | 0 | 0 | 0-100 单位% | 1 | id105 | key105 | 0 | 1
0x00CA | 运营商 | 字符型 | 0x04 | 0 | 1 | 0 | 0 | 字符长度20 | 10 | id106 | key106 | 0 | 1
0x00D4 | 网络类型 | 字符型 | 0x04 | 0 | 1 | 0 | 0 | “0” GSM “2” UTRAN “3” GSM W/EGPRS “4” UTRAN W/HSDPA “5” UTRAN W/HSUPA “6” UTRAN W/HSDPA and HSUPA “7” E-UTRAN | 1 | id107 | key107 | 0 | 1
0x00D5 | 网络状态 | 字符型 | 0x04 | 0 | 1 | 0 | 0 | “0” Not registered. ME is not currently searching a new operator to register to “1” Registered , home network “2” Not registered, but MT is currently trying to attach or searching an operator to register to “3” Registration denied “4” Unknown “5” Registered, roaming | 1 | id108 | key108 | 0 | 1
0x0DF | SIM卡状态 | 字符型 | 0x04 | 0 | 1 | 0 | 0 | 字符最大长度20 含义见备注1 | 1 | id109 | key109 | 0 | 1
0x0E0 | SIM卡ICCID号 | 字符型 | 0x04 | 0 | 1 | 0 | 0 | 字符最大长度50 | 25 | id110 | key110 | 0 | 1
0xF9 | IMEI号（移动设备号） | 字符型 | 0x04 | 0 | 1 | 0 | 0 | 字符最大长度30 | 15 | id111 | key111 | 0 | 1
系统参数区 |  |  |  | 0 | 0 | 0 | 0 |  |  | id112 | key112
0x0150 | 网关时间（分（低字节）、秒（高字节）） | hex | 0x03/0x06 | 1 | 0 | 1 | 0 | BCD码格式 | 1 | id113 | key113 | 1 | 1
0x0151 | 网关时间（日（低字节）、时（高字节）） | hex | 0x03/0x06 | 1 | 0 | 1 | 0 | BCD码格式 | 1 | id114 | key114 | 1 | 1
0x0152 | 网关时间（年（低字节）、月（高字节）） | hex | 0x03/0x06 | 1 | 0 | 1 | 0 | BCD码格式 | 1 | id115 | key115 | 1 | 1
0x0153 | 保留 |  |  | 0 | 0 | 0 | 0 |  | 3 | id116 | key116
通信参数区 |  |  |  | 0 | 0 | 0 | 0 |  |  | id117 | key117
0x0156 | 保留 |  |  | 0 | 0 | 0 | 0 |  | 1 | id118 | key118
0x0157 | 保留 |  |  | 0 | 0 | 0 | 0 |  | 1 | id119 | key119
0x0158 | 波特率（默认9600） | ushort | 0x03/0x06 | 1 | 0 | 1 | 0 | 1：9600 2：14400 3：19200 默认为1 | 1 | id120 | key120 | 1 | 1
0x0159 | bit0 停止位 bit1-2 奇偶校验位（默认无校验） | ushort | 0x03/0x06 | 1 | 0 | 1 | 0 | 0：1位停止位 1：2位停止位 0：无校验 1：奇校验 2：偶校验 默认为0 | 1 | id121 | key121 | 0 | 1
0x015A | 保留 |  |  | 0 | 0 | 0 | 0 |  | 1 | id122 | key122 | 0 | 1
0x015B | 网关类型 | ushort | 0x03/0x06 | 1 | 0 | 1 | 0 | 21：WiFi版本网关 22：以太网RJ45网关 23: 4G网关 24: 4G网关路由 | 1 | id123 | key123 | 0 | 1
0x015C | 配置成功的子设备总个数（更换网关后写入新网关，写入后需要重新寻找设备） | ushort | 0x03/0x06 | 1 | 0 | 1 | 0 | 范围0-32个 | 1 | id124 | key124 | 1 | 1
0x015D | 控制命令禁止和使能（群控在线设备命令，不支持06功能码，必须同时且单独控制0x015D-0x0160的变量） | uint | 0x03/0x10 | 1 | 0 | 0 | 1 | Bit0：地址1 Bit1：地址2 … Bit15：地址32 0：禁止控制，不参与群控 1：使能控制，参与群控 | 2 | id125 | key125 | 1 | 1
0x015F | 控制命令 | uint | 0x03/0x10 | 1 | 0 | 0 | 1 | Bit0：控制地址1 Bit1：控制地址2 … Bit15：控制地址32 0：分闸，1：合闸 | 2 | id126 | key126 | 1 | 1
0x0161 | 群控时间间隔 | ushort | 0x03/0x06 | 1 | 0 | 1 | 0 | 范围100-10000ms （默认200）， 最好用户不要更改 |  | id127 | key127 | 1 | 1
工厂参数区 |  |  |  | 0 | 0 | 0 | 0 |  |  | id128 | key128
0x01D0 | 保留 |  |  | 0 | 0 | 0 | 0 |  | 1 | id129 | key129
0x01D1 | 软件版本号 | ushort | 0x03 | 1 | 0 | 0 | 0 | Y/10（如235表示2.3.5） | 1 | id130 | key130 | 0 | 1
0x01DA | 出厂时间（分（低字节）、秒（高字节）） | hex | 0x03/06 | 1 | 0 | 0 | 0 | BCD码格式 | 1 | id131 | key131 | 0 | 1
0x01DB | 出厂时间（日（低字节）、时（高字节）） | hex | 0x03/06 | 1 | 0 | 0 | 0 | BCD码格式 | 1 | id132 | key132 | 0 | 1
0x01DC | 出厂时间（年（低字节）、月（高字节）） | hex | 0x03/06 | 1 | 0 | 0 | 0 | BCD码格式 | 1 | id133 | key133 | 0 | 1
0x01E5-0x01E8 | 设备ID | ustr | 0x03(不允许写) | 1 | 0 | 0 | 0 | 4，最高byte为FF 5，第二个byte为随机数 其他为出厂时间 | 4 | id134 | key134 | 0 | 1
以太网参数区 |  |  |  | 0 | 0 | 0 | 0 |  |  | id135 | key135
0x230 | IP分配方式（默认1） | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 0：手动，1：自动（DHCP） | 1 | id136 | key136 | 0 | 1
0x231 | MAC地址字节1（高字节），MAC地址字节2（低字节）， | ushort | 0x03（只读） | 1 | 0 | 0 | 0 | 字节1（高字节）,字节2（低字节） | 1 | id137 | key137 | 0 | 1
0x232 | MAC地址字节3（高字节），MAC地址字节4（低字节）， | ushort | 0x03 | 1 | 0 | 0 | 0 | 字节3（高字节）,字节4（低字节） | 1 | id138 | key138 | 0 | 1
0x233 | MAC地址字节5（高字节），MAC地址字节6（低字节）， | ushort | 0x03 | 1 | 0 | 0 | 0 | 字节5（高字节）,字节6（低字节） MAC地址从左到右为字节1,2,3,4,5,6 | 1 | id139 | key139 | 0 | 1
0x234 | 以太网IP地址设置字节1（高字节）,字节2（低字节） | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 字节1（高字节）,字节2（低字节） | 1 | id140 | key140 | 0 | 1
0x235 | 以太网IP地址设置字节3（高字节）,字节4（低字节） | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 字节3（高字节）,字节4（低字节） IP地址从左到右为字节1,2,3,4 | 1 | id141 | key141 | 0 | 1
0x236 | 通信端口号 | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 默认502（modbus TCP） | 1 | id142 | key142 | 0 | 1
0x237 | 以太网子网掩码地址设置字节1（高字节）,字节2（低字节） | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 字节1（高字节）,字节2（低字节） | 1 | id143 | key143 | 0 | 1
0x238 | 以太网子网掩码地址设置字节3（高字节）,字节4（低字节） | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 字节3（高字节）,字节4（低字节） 地址从左到右为字节1,2,3,4 | 1 | id144 | key144 | 0 | 1
0x239 | 以太网网关地址设置字节1（高字节）,字节2（低字节） | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 字节1（高字节）,字节2（低字节） | 1 | id145 | key145 | 0 | 1
0x23A | 以太网网关地址设置字节3（高字节）,字节4（低字节） | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 字节3（高字节）,字节4（低字节） 地址从左到右为字节1,2,3,4 | 1 | id146 | key146 | 0 | 1
0x23B | 以太网modbus主机设置字节1（高字节）,字节2（低字节）（DNS地址，针对MQTT协议） | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 字节1（高字节）,字节2（低字节） | 1 | id147 | key147 | 0 | 1
0x23C | 以太网modbus主机设置字节3（高字节）,字节4（低字节）（DNS地址，针对MQTT协议） | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 字节3（高字节）,字节4（低字节） 地址从左到右为字节1,2,3,4 | 1 | id148 | key148 | 0 | 1
0x23D | TCP通信模式（默认1） | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 0：云模式（MQTT），1：普通以太网模式（modbus TCP，4G不支持此模式） | 1 | id149 | key149 | 0 | 1
0x23E | 保留 | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | 保留 | 1 | id150 | key150 | 0 | 1
0x23F | 485通信模式（默认0） | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | Y（0：正常模式，1：配置模式）--针对主机，配置模式类似于从机模式，可以自由配置信息。 | 1 | id151 | key151 | 0 | 1
0x240 | 失败重连超时 | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | Y（0：表示关闭，1-65535s） 默认180s， 180s没有收到数据，则重新初始化通信，针对modbus TCP有效 | 1 | id152 | key152 | 1 | 1
0x0241 | 电压电流上报变化率 | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | (1-100)% 默认10% | 1 | id153 | key153 | 1 | 1
0x0242 | 功率上报变化率 | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | (1-100)% 默认10% | 1 | id154 | key154 | 1 | 1
0x0243 | 温度上报变化(针对芯片内部温度) | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | （1-100）度 默认10度 | 1 | id155 | key155 | 1 | 1
0x0244 | 频率上报变化 | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | （1-100）Hz 默认10Hz | 1 | id156 | key156 | 1 | 1
0x0245 | 功率因素上报变化 | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | Y/1000（10-1000）*0.001 默认1000（即1） | 1 | id157 | key157 | 1 | 1
0x0246 | 电能上报变化 | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | Y/1000（1-60000）*0.001Kwh 默认10000（即10Kwh） | 1 | id158 | key158 | 1 | 1
0x0247 | 数据周期上报 | ushort | 0x03/0x06/0x10 | 1 | 0 | 1 | 1 | Y/10（1-20000）*0.1分钟 默认150（即15分钟） | 1 | id159 | key159 | 1 | 1
0x248-0x256 | WiFi用户名（预留-not used） | 字符型 | 0x03/0x10 | 1 | 0 | 0 | 1 | 字符最大长度30 | 15 | id160 | key160 | 0 | 1
0x257-0x265 | WiFi密码（预留-not used） | 字符型 | 0x03/0x10 | 1 | 0 | 0 | 1 | 字符最大长度30 | 15 | id161 | key161 | 0 | 1
0x266-0x28D | MQTT域名（或者IP地址） | 字符型 | 0x03/0x10 | 1 | 0 | 0 | 1 | 字符最大长度80 | 40 | id162 | key162 | 1 | 1
0x28E-0x2AB | 用户名 | 字符型 | 0x03/0x10 | 1 | 0 | 0 | 1 | 字符最大长度60 | 30 | id163 | key163 | 1 | 1
0x2AC-0x2C9 | 密码 | 字符型 | 0x03/0x10 | 1 | 0 | 0 | 1 | 字符最大长度60 | 30 | id164 | key164 | 1 | 1
0x02CA | MQTT端口号 | ushort | 0x03/0x10 | 1 | 0 | 0 | 1 | 1个寄存器值 | 1 | id165 | key165 | 1 | 1
0x2CB | Qos | ushort | 0x03/0x10 | 1 | 0 | 0 | 1 | 0，1，2（针对4G卡无效） | 1 | id166 | key166 | 1 | 1
0x02CC | Retain | ushort | 0x03/0x10 | 1 | 0 | 0 | 1 | 遗嘱功能使能和禁止，一直开启 | 1 | id167 | key167 | 0 | 1
0x2CD | Connection Timeout（预留-not used） | ushort | 0x03/0x10 | 1 | 0 | 0 | 1 |  | 1 | id168 | key168 | 0 | 1
0x2CE | Keep Alive Interval（预留-not used） | ushort | 0x03/0x10 | 1 | 0 | 0 | 1 |  | 1 | id169 | key169 | 0 | 1
0x2CF | Clean Session（预留-not used） | ushort | 0x03/0x10 | 1 | 0 | 0 | 1 |  | 1 | id170 | key170 | 0 | 1
0x2D0 | Enable SSL/TLS（预留-not used） | ushort | 0x03/0x10 | 1 | 0 | 0 | 1 |  | 1 | id171 | key171 | 0 | 1
0x2D1-0x2D8 | 预留（TCP相关参数设置） |  | 0x03/0x10 | 1 | 0 | 0 | 1 |  | 8 | id172 | key172 | 0 | 1
0x2D9-0x2FE | 预留 |  |  | 0 | 0 | 0 | 0 |  | 22 | id173 | key173 | 0 | 1
0x2FF | CRC计算值 |  |  | 0 | 0 | 0 | 0 |  | 1 | id174 | key174 | 0 | 1